ENERGY AUDIT CONDITIONAL GRANT REPORT

FOR

Industrial Plant Name

Prepared by

| Company logo | Client logo |
| --- | --- |
| Auditor Name and Address | Client Name and Address |

Under

SUSTAINABLE ENERGY DEVELOPMENT AUTHORITY MALAYSIA

CONFIDENTIALITY

This document contains information for the sole perusal of *Client name* located in *Client address*. All information contained here is prohibited from being copied out. The information here shall not be copied, printed or sold to any 3rd party sources without prior written permission from *Client name*.

DISCLAIMER

*Auditor Name* located in *Auditor address* has no personal or financial interest in supplying or installing equipment for this document.

Table of Contents

GLOSSARY	5

1	EXECUTIVE SUMMARY	6

2	INTRODUCTION	8

2.1	OBJECTIVE	8

2.2	METHODOLOGY	8

2.3	TYPE OF ENERGY AUDIT AND PROCESS	8

2.4	SCOPE OF WORK	8

2.5	TIME SCHEDULE AND AUDIT FRAMEWORK	9

2.6	ENERGY AUDIT EQUIPMENT	9

3	MANAGEMENT OF ENERGY	10

3.1	POLICY AND TARGETS	10

3.2	ENERGY DATA, DOCUMENTATION AND MONITORING	10

3.3	COMPLIANCE TOWARDS REGULATIONS	11

3.4	ENERGY MANAGEMENT TEAM	11

3.5	ENERGY AUDIT TEAM	12

3.6	ENERGY MANAGEMENT MATRIX REVIEW	12

3.7	OPERATIONS AND MAINTENANCE SYSTEM REVIEW	13

4	INDUSTRIAL PLANT DESCRIPTION	14

4.1	GENERAL DESCRIPTION	14

4.2	PRODUCTION TYPE	14

4.3	PROCESS/S FLOW DESCRIPTION	14

4.4	OVERVIEW OF ACTIVE SYSTEM	16

5	ELECTRICAL SUPPLY INFORMATION AND ANALYSIS	17

5.1	TARIFF REVIEW	17

5.2	MAXIMUM DEMAND REVIEW	17

5.3	VOLTAGE LEVEL	17

5.4	HISTORICAL ENERGY CONSUMPTION	17

5.5	POWER FACTOR	18

6	ENERGY CONSUMPTION INFORMATION AND ANALYSIS	21

6.1	ELECTRICAL SUPPLY	21

6.1.1	SYSTEM DESCRIPTION	21

6.1.2	BUILDING LOAD PROFILE ANALYSIS	21

6.1.3	OBSERVATION AND FINDINGS	22

6.2	CHILLED WATER SYSTEM AND DISTRIBUTION	22

6.2.1	SYSTEM DESCRIPTION	22

6.2.2	LOAD PROFILE ANALYSIS	23

6.2.3	OBSERVATION AND FINDINGS	24

6.3	COMPRESSED AIR SYSTEM AND DISTRIBUTION	24

6.3.1	SYSTEM DESCRIPTION	24

6.3.2	OBSERVATION AND FINDINGS	26

6.4	BOILER/HOT WATER SYSTEM AND DISTRIBUTION	28

6.4.1	SYSTEM DESCRIPTION	28

6.4.2	OBSERVATION AND FINDINGS	29

6.5	PROCESS EQUIPMENT	30

6.5.1	SYSTEM DESCRIPTION	30

6.5.2	OBSERVATION AND FINDINGS	30

6.6	AIR CONDITIONING AND MECHANICAL VENTILATION SYSTEM	30

6.6.1	SYSTEM DESCRIPTION	30

6.6.2	BLOWER FAN SPECIFIC POWER	31

6.6.3	AIR CHANGE RATE AND AHU CAPACITY ANALYSIS	31

6.6.4	INDOOR AIR QUALITY	32

6.6.5	TEMPERATURE AND RELATIVE HUMIDITY	32

6.6.6	OBSERVATION AND FINDINGS	33

6.7	LIGHTING SYSTEM	33

6.7.1	SYSTEM DESCRIPTION	33

6.7.2	LUX LEVEL	34

6.7.3	OBSERVATION AND FINDINGS	35

6.8	PLANT MANAGEMENT SYSTEM	35

6.8.1	SYSTEM DESCRIPTION	35

6.8.2	OBSERVATION AND FINDINGS	35

6.9	CO-GENERATION BY BIOGAS/DIESEL/OTHERS AND DISTRIBUTION	35

7	LOAD APPORTIONING AND ENERGY INDEX	36

8	ENERGY SAVING MEASURES AND FINANCIAL EVALUATION	37

ESM 1: Use Room/Return Air Humidity Input to Automatically Control the Glycol Chiller	37

8.1.1	SUMMARY OF ENERGY SAVING MEASURES	38

9	ENERGY SAVING MEASURES IMPLEMENTATION PLAN (3 YEARS)	39

10	CONCLUSION	39

11	VERIFICATION	40

# GLOSSARY

In this report, the following words and abbreviations shall be defined as follows:

| Words/Abbreviations | Definition |
| --- | --- |
| Audit | Energy Audit |
| TRH | Ton Refrigerant Hour |
| TNB | Tenaga Nasional Berhad |
| kWh | Kilo Watt hour |
| MD | Maximum Demand |
| PF | Power Factor |
| ESM | Energy Saving Measures |
| BCS | Building Control System |
| DDC | Direct Digital Control |
| BEI | Building Energy Index |
| LEI | sample Lighting Energy Index |
| ACEI | Air Conditioning Energy Index |
| PEI | Plug Load Energy Index |
| OTTV | Overall Thermal Transfer Value |
| RTTV | Roof Thermal Transfer Value |
| WWR | Window to Wall Ratio |
| CCTV | Closed Circuit Television |
| ACMV | Air Conditioning Mechanical Ventilation |
| COP | Coefficient of Performance |
| CHW | Chilled Water from GDC |
| CHWP | Chilled Water Pump |
| HEX | Heat Exchanger |
| AHU | Air Handling Unit |
| FCU | Fan Coil Unit |
| VAV | Variable Air Volume – used with AHU and FCU |
| VRV | Variable Refrigerant Volume – used in Telco Rooms |
| VSD | Variable Speed Drive |
| EnMS | Energy Management System – ISO 50001 |
| DPM | Digital Power Meter |
| BCiS | Building Consumption Input System |

# EXECUTIVE SUMMARY

Brief summary of the audit, building, key systems audited, consumption and breakdown of consumption.

Example

This report represents the findings of the Energy Audit conducted by Auditor name for Client name, between date. The systems audited include Boiler, Compressed Air, Cooling tower, Mill, Air Conditioning for plant and Motors. Data for other equipment such as lighting and office air conditioning and office equipment were based on assumptions.

Plant name has an estimated total gross building area of 32,375m2, net floor are of 31,611m2 and an air-conditioned area of 23,677m2. The annual electricity consumption obtained from the historical TNB billing data for the year 2019 is 5,5130955kWh costing RM2,921,940. Plant name is a single story building with a mezzanine floor.

Briefly describe the chart.

Example

The load apportioning for the plant is listed in the table below and shown in the corresponding graph. The highest significant energy uses are the compressed air followed by the cooling tower, air conditioning for the plant and motors.

| Description | Energy kWh |
| --- | --- |
| Air compressor | 1847221.2 |
| Boiler | 591616.87 |
| Cooling tower | 890714.88 |
| Mill | 301754.97 |
| Motors | 664,240 |
| Air conditioning (plant) | 772960 |
| Air conditioning (office) | 56861 |
| Lighting (plant) | 335022 |
| Lighting (office) | 32941 |
| Office equipment | 19764 |

sample

Brief summary if energy savings recommendations.

Example

Seven (7) Energy Saving Measures (ESMs) have been identified in the Energy Audit conducted. By implementing all recommended Energy Saving Measures, the energy consumption for Building name can be reduced by about 23%, or 52,416kWh per year representing RM15,096 in monetary value. The estimated budget cost of implementing the Energy Saving Measures is RM27,042 with a payback period of about 1.79 years. The estimated savings, budget costs and Simple Payback Period of all recommended Energy Saving Measures, are listed in the table below.

sample

Brief summary of the existing SEC and the new reduced SEC.

Example

Using the estimated current annual energy consumption 232,050kWh and occupied areas, the current Specific Energy Consumtion (SEC) is xxx kWh/product and after implementing all recommended Energy Saving Measures to xxx kWh/product. The percentage reduction is 41%.

41% Reduction

sample

# INTRODUCTION

Brief explanation on functions, operation hours, occupancy rate, etc.

Example

The Industrial sector is the largest energy consumer in Malaysia amounting to 50% of the total energy consumed in the country. The energy audit is a major component of an Energy Management System (EnMS) and has to be carried out continuously to ensure continuous of monitoring, control and management of energy use as well as reduction in energy consumption.

Client name, intends to conduct a detailed energy audit exercise for the plant in location. Client name has appointed Auditor name, the energy service company to conduct the energy audit.

Building name was built in 1998 and has been in full operation for the last 25 years. It comprises of a 12m high factory lot with a 250m2 mezzanine floor for the administration office. The plant is used solely for the production of plastic injection moulded speaker boxes. A 10,285m2 warehouse is located in an adjacent building. With a capacity of 200 factory workers, the plant operates on a 24 hour shift, with 3 working shifts daily.

Building Description

| Building Name: | Client name |
| --- | --- |
| Address: | Client address |
| Building Use: | Factory and warehouse |
| In operation since: | 1998 |

OBJECTIVE

Brief explanation

Example

The objective of a detailed energy audit study is to determine the energy performance of the plant through detailed measurement and analysis, and identify potential savings that can optimize energy consumption, reduce wastage and reduce the operating costs of the plant.

The compiled data and findings from this audit are to be used to assist Client name to monitor and operate the plant more efficiently and at the same time identify potential energy saving measures for improved performance and optimization of equipment operation.

METHODOLOGY

Brief explanation/As per SEDA Guideline

Example

The methodology used for the energy audit is based on SEDA’s guideline shown below. The kick off meeting was held on date/time. All desktop data was made available to the energy audit team prior to the on-site audit works. The on-site audit works was held between date and date. There were some delays due to unforeseen circumstances, but the energy auditor managed to complete all works within the stipulated timeframe.

The data collection and analysis of all data was completed within the timeframe given. The energy baseline was determined from the past year TNB bills analysis and was cross referenced with the 2 week data logging that took place at the beginning of the audit. During the on-site survey and investigation, several weaknesses on energy wastage were identified. These are listed in the energy supply and consumption analysis sections. Recommendations for energy saving opportunities, financial evaluation and projected implementation was completed in the last week before submission of the draft report and are highlighted in the energy saving and financial evaluation, and implementation sections of the report. Refer figure below.

TYPE OF ENERGY AUDIT AND PROCESS

Brief explanation/As per SEDA Guideline

Example

The energy audit conducted was a Detailed Energy Audit or also known as ASHRAE Level II which included a detailed survey of the premises. Detailed data collection was obtained through on-site measurements such as power data logging and on-the-spot measurements. The energy audit focussed on significant energy use including the plant process, boiler system, compressed air system, hydraulic press and large motors.

The detailed analysis was done based on the data collected with estimated energy use values and costs to develop a proposal for implementation of energy saving projects.

SCOPE OF WORK

Brief explanation/As per SEDA Guideline

Example

The scope of works covered in the energy audit are as per SEDA’s guideline listed below.

Energy Management of the installation:

- Review of operation and maintenance contract including budget required

- Review of existing energy efficiency policies or if an energy management system was in place

- Review all documents pertaining to energy usage

- Review organizational structure and resource allocation for energy management

- Obtain all installation information

- Energy management matrix

Energy supply information:

- Tariff structure, energy consumption and costs

- Maximum demand and costs

- Voltage supply level from TNB and Consumer

- Historical supply information for the past 3  years

- Power factor information

Energy usage information:

- Conduct overall power distribution profile of the premise including the main electrical powered equipment, monitoring and analysis for audited system at least for a period of 14 days

- Conduct electrical energy load loss survey and site evaluation for the audited system (refer to energy audit proposal and scope submitted and approved by the government / Energy Audit Conditional Grant Committee)

- Study on the energy usage for all/selected equipment and systems

- Establish electricity consumption distribution based on equipment/systems e.g. heating and cooling system, lighting, chiller, boiler, compressor and etc. in kWh or equivalent, and percentage

- Identify and study operating schedule or parameters that affecting the energy consumption

- Establish Specific Energy Consumption (SEC) for each installation

- Identify control system being used (automatic/manual)

- Conduct power measurement and analysis

- Carry out necessary measurement for relevant parameters

- Conduct pump system efficiency (depend to site condition)

- Calculate overall System Coefficient of Performance

- Fans and Blowers

  - Describe the system(s) briefly

  - Study the system schedule and operation hours

  - Describe observations and findings

    - Lighting

      - Prepare a list of types of lamps used and its rated power at internal and external areas (fluorescent, CFL, LED etc)

      - Study lighting operating schedule

      - Conduct measurement and analysis of lighting fitting layout and lux level

      - Conduct power measurement and analysis

      - Conduct lighting control systems and zoning analysis

- Air Compressor System

  - Provide air compressor system diagram

  - Identify the number of air compressor used in the system

  - Study the air compressor operating schedule

  - Provide and explain load profile for each compressor

- Electrical Motor, Pumps and Production Machine

  - Show the list of machine/equipment types and quantity

  - Describe the system and operations for each type of machine/equipment

  - Provide and explain load profile for each machine/equipment

  - Describe observations and findings for each machine/equipment

    - Ventilation System / Indoor Air Quality & Infiltration

      - Identify control system being used (automatic/manual)

      - Study ventilation system operating schedule

      - Conduct air flow measurement and analysis

      - Conduct energy and power measurement for selected fan

      - Conduct CO and CO2 level measurement and analysis

      - Analysis on zoning and air change measurement

    - Plant/Building Automation System (BAS)

      - Confirm the function of the BAS facilities and parameters being controlled

      - Perform measurement variation study between actual and the reading in the system

      - Study the characteristic of BAS in term of monitoring, control and reporting

- Process Equipment

  - Survey and identify the types of process equipment in each room and area with its power consumption (rated capacity, performance rating etc)

- Steam Generation by Biogas/Diesel/others and Distribution System

  - Explain the generation and distribution system

  - Explain the energy consumption and load profile for each generator and distributor system

Energy saving potential and measures (ESM)

ESMs (action plan and estimated time required to implement the measure recommended, amount of saving and cost of implementation). The ESMs addresses energy management and energy efficiency. Renewable energy can be included but is not part of the Energy Audit Conditional Grant scope.

  - Energy Saving Measures and Recommendations

    - Text

    - Describe the proposed energy savings measures

    - A list of equipment potential credible suppliers

- Chart

    - Graphical illustration

    - Existing and proposed system (if applicable)

    - Photo

      - Existing situation

      - Proposed equipment sketches or sample photo from manufacturer catalogue

  - List opportunities for electrical energy saving measures identified (saving to systems/equipment/control/monitoring/management) in tables

    - Each measure should have tables consisting:

      - The assumptions used in estimating the energy savings

      - The methods used in estimating the savings

      - Technical calculation

      - The conditions to achieve the savings

  - Identify detailed methods to achieve savings/electrical energy reduction according to:

    - No cost/ min cost – changes of time and operation methods, minor repair / improvements

    - Low and high cost or Medium cost - based on percentage

    - High cost measure

  - Estimate total potential electrical energy saving in kWh

  - Propose an action plan and the estimated time required to implement each saving measure if the management decides to implement it.

  - Propose methods of measurement and calculation to quantify energy savings based on identified saving potentials.

Financial analysis

The basic life cost cycle analysis for the proposed energy saving measures (SPP, ROI)

- Measures and costs

- Each measure and potential saving

- Expected return of investments from financial evaluation tools (e.g. SPP, ROI etc.) in years or months.

Financial and Energy Saving Measures Implementation Plan for Owner to Implement (3 years)

- 1st Year, estimated implementation cost and savings.

- 2nd Year, estimated implementation cost and savings.

- 3rd Year, estimated implementation cost and savings.

The ESMs implementation planning addresses energy management and energy efficiency. Renewable energy can be included but is not part of the Energy Audit Conditional Grant scope. The total cost and savings from renewable energy are not counted as implementation and savings achieved under this EACG scheme.

TIME SCHEDULE AND AUDIT FRAMEWORK

Example

The time schedule for carrying out the audit is a per table below. The audit started on 2 Mar 2022 and was completed on 20 May 2022. There was a 2 week delay due to shutdown of some of the processes in the plant for maintenance works.

sample

Jan

Feb

Mar

Apr

ENERGY AUDIT EQUIPMENT

List of equipment

The type of audit equipment is as per table below:

| Equipment | Function |
| --- | --- |
|  | Data Loggers / Power Monitoring Meter (Single/3phase) Measures electrical power parameters such as kWh, kVArh, kVAh and power factor (pf) Other parameters measured include Frequency, Maximum Demand, Voltage, Current and Power Quality It is normally used to check for electrical faults and if the phases are balanced. |
|  | Thermohygrometer (Temperature/ Relative Humidity Meter) Measures the temperature as well as the relative humidity of an area. It is normally used for air-conditioning design or investigations. Usually measured in °Celsius/°Fahrenheit and %Relative Humidity |
|  | Anemometer Measures the air velocity flowing through a channel. It is normally used for measuring air flow in an air handling unit, at duct intakes and openings such as doorways. Usually measured in m/s. |
|  | Tachometer Measures motor speed on shafts. It is also used to calculate motor efficiency. |
|  | Ultrasonic Flowmeter Measures the velocity of fluid or air over a known area. It is normally used for measuring chilled water flow or compressed air in pipes. Usually measured in l/s. |
|  | Flue Gas Analyser Measures concentration of O2, CO2 to determine indoor air quality – for air conditioning and ventilation. |

# MANAGEMENT OF ENERGY

POLICY AND TARGETS

Policy declaration and brief description of targets and timeframe

Example

Client name has an Energy Management Policy in place. The Client is committed to ensuring that all activities in the company are carried out sustainably. Some of the commitments are listed below:

- Provide adequate training for employees

- Employ energy conservation and saving practices to all levels of the company

- Committed to make information on energy conservation and resource available to all levels of the company

- Committed to comply with local legal requirements where necessary

- Continuously monitor and control energy consumption

- Identify energy wastages and take corrective measures to eliminate them

- Procure energy efficient products

- Periodically review and improve goals for a successful sustainability program

Targets for the energy management program for Client name are:

- Real live tracking of energy consumption and maximum demand control

- Reduce energy cost by 20% within the next 3 years

  - Through implementing energy saving measures

  - Procuring energy efficient equipment

  - Upgrading lighting system and control

  - Training to continuously optimize energy consumption

ENERGY DATA, DOCUMENTATION AND MONITORING

Describe the level of documentation available in the organization, policies, records, regulations, guides, training in relation to energy management

Describe monitoring of energy use procedures, energy performance indicators, effectiveness of action plans in achieving objectives and targets, evaluation of actual vs expected energy consumption – results from monitoring and measurement should be recorded

Example

The energy consumption documents as well as information pertaining to energy consumption such as policy, regulations, procurement documents, design and installation drawings, testing and commissioning reports and financial evaluation reports are kept in the administration office under the purview of the Registered Electrical Energy Manager (REEM), name and is accessible to the top management and energy management team.

The REEM sees to monitoring the energy consumption of the company. Two (2) energy audits have been conducted in the past 8 years and some minor energy saving implementation projects have been carried out, i.e. replacing LED in certain areas and purchasing 5-star appliances for the office.

The REEM also reports the energy consumption to Suruhanjaya Tenaga, Malaysia every 6 months as per requirement.

COMPLIANCE TOWARDS REGULATIONS

Describe evaluation procedures in complying with legal requirements in relation to energy use and consumption, records

Example

The company is subject to EMEER 2008:

- Is applicable to large energy users, i.e. 300,000kWh consumption for at least 6 months

- Appointment and notification of Electrical Energy Manager

- Electrical Energy Management Policy

- Energy Audit

- Recommendations for electrical energy management

- Monitoring and keeping of records

- Periodical reporting

ENERGY MANAGEMENT TEAM

List names, position and role

Example

The energy management team is headed by Manager name and assisted by his team members as shown in the Chart. The CEO overlooks the whole energy management activities carried out by the company. The team meets once a week to discuss issues pertaining to energy consumption and production output. The activities are mainly carried out by the Engineer and reported back to the energy management team. The Engineer is also a Registered Electrical Energy Manager (REEM).

ENERGY AUDIT TEAM

List names, position and role

Example

The energy audit team is headed by auditor lead and assisted by his team members as shown in the Chart. The Energy Auditor is assisted by a team of experts from various fields of expertise to carry out the various types of energy audit measurements. The data is compiled by the Energy Manager who analysed the data and prepared the energy audit report.

ENERGY MANAGEMENT MATRIX REVIEW

EM matrix may be used to determine level of energy management practiced and can be used as a guide for improvement

Example

An assessment was carried out to determine whether an Energy management system (EnMS) is in place in the plant. Currently there is no official system but there have been a few energy saving exercises carried out in the past few years. One such exercise is replacing the older warehouse lighting of 36W bare channel fluorescent lamps with 18W LED lamps. A digital power meter (DPM) is also installed to measure the energy consumption so that savings can be accounted for.

An energy management matrix was used to determine the scope of energy practices being implemented in the plant.

|  | Policy and Systems | Organization | Motivation | Information System. | Training and awareness | Investment |
| --- | --- | --- | --- | --- | --- | --- |
| 4 | Formal energy /environmental policy and management system, action plan and regular review with commitment of senior management or part of corporate strategy | Energy / environmental management fully integrated into management structure. Clear delegation of responsibility for energy use | Formal and informal channels of communication regularly exploited by energy / environmental manager and staff at all levels | Comprehensive system sets targets, monitors materials and energy consumption and wastes and emissions, identifies faults, quantifies costs and savings and provides budget tracking | Marketing the value of material and energy efficiency and the performance of energy / environmental management both within the organization and outside it | Positive discrimination in favour of energy / environmental saving schemes with detailed investment appraisal of all new build and plant improvement opportunities |
| 3 | Formal energy / environmental policy but no formal management system and with no active commitment from top management | Energy / environmental manager accountable to energy committee, chaired by a member of the management board | Energy / environmental committee used as main channel together with direct contact with major users | Monitoring and targeting reports for individual premises based on sub-metering / monitoring but savings not reported effectively to users | Programme of staff training, awareness and regular publicity campaigns | Same pay back criteria as for all other investments. Cursory appraisal of new build and plant improvement opportunities |
| 2 | Unadopted / informal energy / environmental policy set by energy / environmental manager or senior departmental manager | Energy / environmental manager in post, reporting to ad-hoc committee but line management and authority unclear | Contact with major users through ad-hoc committee chaired by senior departmental manager | Monitoring and targeting reports based on supply meter / measurement data and invoice. Env / energy staff have ad-hoc involvement in budget setting | Some ad-hoc staff awareness and training | Investment using short term pay back criteria mostly |
| 1 | An unwritten set of guidelines | Energy or environmental management the part-time responsibility of someone with only limited influence or authority | Informal contacts between engineer and a few users | Cost reporting based on invoice data. Engineer compiles reports for internal use within technical department | Informal contacts used to promote energy efficiency and resource conservation | Only low-cost measures taken |
| 0 | No explicit policy | No energy environmental manager or any formal delegation of responsibility for env/energy use | No contact with users | No information system. No accounting for materials and energy consumption and waste | No awareness raising of energy efficiency and resource conservation | No investments in increasing environmental performance or energy efficiency in premises |

*To remarks current status of the energy management matrix and target of the building

OPERATIONS AND MAINTENANCE SYSTEM REVIEW

List scope of works involved for energy management

The Operation & Maintenance Contract for the plant covers the following:

- Monitoring and managing energy usage and conservation

- Steps taken and opportunities identified to reduce energy consumption

- Operate a continuous improvement process on energy usage

- Review annually the plant performance against current best practice and institute an energy conservation program for the following year

- Demonstrate innovation in the efficient use of energy and materials to provide a sustainable environment

- Conduct energy audits

- Implement energy saving opportunities in stages

- All relevant building energy parameters shall be monitored before and after the energy saving measures are implemented

- An energy saving baseline shall be established for comparison

- Conduct training for awareness to staff

- Integrate best energy practice in the daily operation and servicing of the plant

# INDUSTRIAL PLANT DESCRIPTION

GENERAL DESCRIPTION

Brief description of the plant

Example

The plant is located in location. It comprises of a 12m high factory lot with a 250m2 mezzanine floor for the administration office. The plant is used solely for the production of plastic injection moulded speaker boxes. A 10,285m2 warehouse is located in an adjacent building. The plant comprises of the compressed air, boiler and process equipment. The electrical substation is located just at the back of the factory block. The administration office holds the Production, Engineering and Logistics office. An adjacent building holds the warehouse where the raw materials and finished goods are stored. With a capacity of 200 factory workers, the plant operates on a 24 hour shift, with 3 working shifts daily.

The factory and warehouse blocks materials are mainly aluminium and partially concrete. The aluminium roof has a skylight to allow daylight into the plant. The Gross Floor Area (GFA), Net Floor Area (NFA) and Air Conditioned Area of the building is given below in the Table.

Picture/s of building – side, front, top views

| Description | Gross Floor Area | Net Floor Area | Air-Conditioned Area | Height (m) |
| --- | --- | --- | --- | --- |
| Client name | 32,375 | 31,611 | 25,321 | 12 (1 floor) and 1 mezzanine floor |

PRODUCTION TYPE

Explain briefly the products manufactured by the plant including sample pictures of the products starting from the first year of production until now

PROCESS/S FLOW DESCRIPTION

Briefly explain the process flow of production including graphical figures to show the steps of the process

Example

The diagram below shows the process flow for the production of corrugated carton boxes.

Paper Roll

Paper rolls are brought in from paper roll manufacturers. The paper is made from recycled paper, bleached and pressed into paper sheets.

Corrugator

The corrugating machine will heat up the glue using steam from the boiler to glue the corrugated sheets together. Depending on production requirements, there are 3 types of corrugated board based on number of layers and flute sizes.

Sheet Boards

The sheet boards are cut according to size to be sent to the printer and die cutter or slotter machines for the final touches.

Stitching/Gluing

The finished sheet boards are then sent for stitching or gluing before being packed for delivery.

OVERVIEW OF ACTIVE SYSTEM

General explanation of each active system that was involved during energy audit. Please include photos/diagram/schematic of the overall view of the electrical distribution reflecting the energy balance in the premise. This is to show the power/load capacity and energy flows, how and where it been used (incoming and outgoing/consumed)

Example

The systems that were audited only cover the Corrugator, Boiler and Compressed air systems.

Boiler

Briefly describe boiler function for the process plant and what was audited

Compressed air

Briefly describe Compressed air system and function for the process plant and what was audited

Corrugator

Briefly describe corrugator process and what was audited

# ELECTRICAL SUPPLY INFORMATION AND ANALYSIS

TARIFF REVIEW

Describe tariff system used

Example

The energy consumption charge is 36.5sen per kWh and maximum demand charge is RM30.30 per kW. The average cost is RM0.43/kWh.

| Year | Energy Rate (RM/kWh) | Maximum Demand Rate (RM/kW) |
| --- | --- | --- |
| Jan 2014- present | RM0.365 | RM30.30 |

MAXIMUM DEMAND REVIEW

Describe maximum demand status and means to control monthly maximum demand levels

Example

There is currently no maximum demand control in place.

VOLTAGE LEVEL

Example

The building is supplied by six (6) 3150kVA, 11kV/433V Transformers and three (3) 2.5MVA, 11kV/3.3kV Transformers.  In addition, there are three 1.25MVA Standby Generator sets located outside the HT/LV switch room at the ground floor of the building.

HISTORICAL ENERGY CONSUMPTION

Describe energy consumption and cost

Example

The historical energy consumption of the building can be found in the monthly electricity bills for the past 2 years, i.e., 2013 to 2014. Chart below shows the Energy Consumption and Energy Costs for the building from 2013 to 2014.

sample

Describe energy consumption, maximum demand and costs

Example

The energy consumption is seen at the lowest in the month of July as there were many holidays during that month.

sample

POWER FACTOR

Example

There is no power factor penalty.

Regression Analysis

To do analysis for regression analysis

Example

There are there (4) major factors related to Building Energy Index (BEI) determined for building name which are as follows:

- Independent variable such as (No of working days, no of operations and etc)

- Independent variable

Table below shows the data for the independent variable and the dependent variable is operating throughout the month and year in 2023.

| Month 2021 | Independent variable | Independent variable | Independent variable | Energy Consumptions (kWh) |
| --- | --- | --- | --- | --- |
| Jan |  |  |  |  |
| Feb |  |  |  |  |
| Mar |  |  |  |  |
| Apr |  |  | sample |  |
| May |  |  |  |  |
| Jun |  |  |  |  |
| Jul |  |  |  |  |
| Aug |  |  |  |  |
| Sep |  |  |  |  |
| Oct |  |  |  |  |
| Nov |  |  |  |  |
| Dec |  |  |  |  |

Table 5: xxx

To do analysis for single and multiple regression

Multiple Analysis using Three (3) Variable Factors

Multiple Regression Analysis was performed using Microsoft Excel for number of patients, number of working days as the multiple independent variables. Table below shows the summary of output of the Regression Analysis. From Table, the y-intercept, the coefficient of each independent variable as in Equation 1, R-square (coefficient of determination) and standard error of the mathematical modelling can be obtained.

sample

Table 5: Regression with Three Variables (independent variable)

Y = 47.57x1 + 18439.21x2 +209.85x3 + 4938.49

Where,

Y 		= Electricity consumption (kWh)

X1 		= independent Variable

X2 		= independent Variable

X3		= independent Variable

4938.49	= Base load

The R2 = 0.833 is more than 0.75. All these 3 factors will be considered in monitoring the energy consumption

# ENERGY CONSUMPTION INFORMATION AND ANALYSIS

ELECTRICAL SUPPLY

### SYSTEM DESCRIPTION

Describe system

Example

The building has two 11kV/415V TNB Incomers supplying power to the building. The building electrical supply and distribution system then feeds into two transformers Tx1 and Tx2. Both transformers are rated at 2500kVA/3500kVA. The transformers feed 2 MSBs labelled MSB1 and MSB2 respectively. The Annex building also obtains its power supply from the main building MSBs.

Two (2) 1250kVA Gensets are used for back-up supply in case of power failure. The two gensets are on standby during power failure.

sample

### BUILDING LOAD PROFILE ANALYSIS

Describe load profile

For systems with more than 1 MSB, please total up the total MSB loads for the total building load profile

Example

Using a number of specialized load data logging devices, the auditor has over the period between 15 and 30 March 2022 to log the total building load cycle.  Further, using the current building kW sub-meters and clamp on meter, the consultant team has reliably established typical daily load cycles as shown below.

sample

### OBSERVATION AND FINDINGS

During the audit, the energy audit team identified air conditioning equipment running for 24hours. The weekday load profile shows that there is a baseload of approximately 340kW and the peak load is 589kW.

CHILLED WATER SYSTEM AND DISTRIBUTION

### SYSTEM DESCRIPTION

Describe system

Example

The air conditioning system in the building is supplied by a number of air handling units in several plantrooms around the building, which serve manufacturing area, offices, canteen and certain parts of general area of the building.  The air conditioning system components include:

- Six (6) water-cooled chillers, cooling towers, chilled water pumps and condenser water pumps located at the air conditioning plant, outside the manufacturing block.

- Forty (40) air handling units (AHUs) located in the building AHU plant rooms on each floor

- Three Hundred and Eighty-Six (386) fan coil units (FCUs)

- Twelve (12) package air conditioners (PAUs).

The air conditioning for the plant is run for 24 hours a day.

sample

### LOAD PROFILE ANALYSIS

Describe load profile

Example

The chilled water is on a continuous 24-hour supply to the building. This chilled water is metered with a Calorimeter, which is sited in the Chilled Water Pump room.

Ultrasonic Flow Rate Meters were used to measure:

- 24 hours supply and return chilled water temperature

- 24 hours chilled water flow rate

These measurements were for a 1-week time period.

- Electricity power to the pumps

- Electricity frequency to the pumps

These measurements were taken with the instruments listed below.

| Equipment | Purpose |
| --- | --- |
| Temperature Logger and Probe | To measure temperature and time |
| Ultrasonic Flow Rate Meter | To measure flow rate |
| Multimeter | To measure amperes |

Using the above temperature logger and probe together with the ultrasonic flow meter, the 24 hours chilled water supply was measured for its supply and return temperatures and its flow rates.

The daily 24hour temperature and flow rate data is used to confirm the:

- Average supply and return chilled water temperature

- Average temperature differential (∆T)

- Profiling the flow rate of the supply and return chilled water

sample

sample

### OBSERVATION AND FINDINGS

Evaluate Chiller COP and System COP

Example

From the chiller plant energy audit works, it can be concluded as the following;

A week data measurement of chiller plant shows that COP of chiller No 1 is 4.7 and COP of chiller No 2 is 4.5. Based on the System COP chart below, the chillers are considered to still be within ‘Good’ range.

Average chiller COP

Chiller No 1:	4.7

Chiller No 2:	4.5

Chiller No 3:	4.2

- Average leaving chilled water temperature for all chillers are also high (9.6oC & 9.5oC respectively for chiller 1 & 2). This indicates inability of both chillers to produce chilled water temperature at set point (7.0oC). Leaving condenser water temperatures are also at the high side, 37oC against chiller rated condenser leaving temperature of 35oC.

COMPRESSED AIR SYSTEM AND DISTRIBUTION

### SYSTEM DESCRIPTION

Example

The compressed air system used in Building name building comprises three (3) 21.2 kW Ingersoll Rand compressors.  All three compressors are continuously running under different operation modes.  One of the compressors is fully loaded and the second is operated in loaded and unloaded mode in accordance to the compressed air demand and the third compressor is run as a hot reserve in case if one of the loaded compressors fails. In addition, there is one diesel driven compressor used as a standby unit during the shutdown.

Air compressors supply compressed air at 125 psi (8.6 bar) and the pressure of the compressed air at the manufacturing equipment is 105 psi (7.2 bar). According to the operator of the compressed air system, a low pressure alarm will operate at 89 psi (6.14 bar) and manufacturing equipment will shut down when the pressure drops to 85 psi (5.86 bar).

Compressed Air System Schematic

A brief site assessment of the existing compressed air equipment was conducted and some preliminary data logging of the facility’s air pressure, compressor amps and power usage. Note that the estimates are based on data taken over a 7-day measurement period and projected forward to create an annual profile. The readings and observations during the measurement period show the compressed air system was operating at estimate about 1.12 m3/min. with the 21.2 kW compressors in full load.

The air pressure was highly variable due to the high differential pressure drop across the compressed air system clean up equipment (dryers, pre- & after-filters etc). and plant operation. The plant possibly has air quality problems (water in the pipes) due to high dryer inlet air temperatures which causes overloading.

The flow rates measured exceed the minimum requirements of a typical plant mgps. The minimum required flowrate for process lines 1 to 5 is 350L/min at 7 barg (101.5 psi). The minimum requirement flowrate for the process lines 6 to 9 is 80L/min at 4 barg (58 psi).

Some significant air loads may be inappropriate, causing the compressor to be loaded near its full capacity. Significant improvements are possible. Refer Figure below for discharge flow rates.

Discharge flow rates

### OBSERVATION AND FINDINGS

Compressor:-

- The 3 units of 21.2kW compressors was logged during the audit.

- The 21.2kW compressor controller auto sequencer configurations have setting of the auto restart time period that is short, dependent on the minimum tank pressure of 9.0 barg (130.5psi), of approximately 10 minutes, duration. This causes frequent start/stop. About 5-6 start/stop sequences per hour was detected during the assessment period. It is a good energy efficiency strategy for small-capacity systems.

- Slow blow down, high unload kW, of approximately 5kW, causes inefficiency in compressed air systems. Both compressors showed poor turn down. The consumption was about 50 - 75% power during unload. Further investigation and servicing on the compressor is recommended.

Storage tank:-

- The installed tank is an appropriate size in this plant.

- At the nominal compression pressure of 10 barg (145 psi), there is 15,000 litres of air.

Compressed Air Distribution

The pressure drop to the process lines is about 5-7 barg (72.5 – 101.5 psig). This indicates pressure drop over many bends and valves in the piping network.

Artificial demand

The compressed air system pressure can be reduced to achieved compressed air energy optimization as the plant can reduce and remove un-necessary bends and valves in the existing piping network. These un-necessary bends and valves will reduce the air pressure at the existing delivered pressure setting. Stable pressure and consistent flow is needed.

Compressed Air System Cost Estimate

The electrical input to the compressed air system, the airflow output and system pressures were monitored using data loggers. From this, an approximate annual electrical operating consumption was calculated. The baseline power usage of approximately 5kW can be seen. Refer Figure below.

Energy usage for 24-hour period on 5 May

The data recorded by the instrumentations show that the total annual energy consumption for compressed air is about 41,600 kWh at a weekly use of 800kWh. Average facility air loading appears to be about 1.12 m3/min produced at an average of 9.5 barg (after the dryer and inline filter).

Using a utility rate of RM0.53 taken from the most recent power utility electrical billing, the cost of operating the compressed air system calculates to about RM 22,000 per year not including typical maintenance costs. This will be used as the base case for savings calculation purposes.

Compressor Operating Mode

The compressors were on managed by a sequencer controller to rotate compressor change over to equalize hours of operation of the compressors. Unloaded power consumption, about 5 kW, is much higher than it should be, possibly due to problems with the internal blow down circuit.

During assessment period, the 21.2 kW compressor was recorded running unload about 50 - 75% of time, consuming power but not producing compressed air.

Compressor Control

The data logger showed plant compressed air usage varied for 0.91 m3/min to 1.67 m3/min during the assessment period.

A VSD compressor is recommended because it would be more energy efficient in partial load. Saving can be achieved because VSD compressor does not have waste unload run time, the turn down almost proportional to flow reduction.

Compressor Standby Capacity

The estimate average utility capacity is about 1.12 m3/min and the dynamic demand flow recorded or logged during the assessment period was 1.67 m3/min.

Compressor Condition

The two 21W compressors are about 20 years.  The compressors flow capacity might have dropped due to machine age. The compressors may show some reliability and stability issue.

Compressor Discharge Pressure

The average compressed air system pressure at the process line was 5 - 7barg (72.5 – 101.5 psig). If pressure could be lowered by 10 psi, that energy consumption saving about 5 % would be gained. For a relatively small compressor configuration here in HS, it is not recommended for the installation of a pressure/flow controller. The greater pressure stability and pressure reduction it provided is not vital in a plant.

Leaks, Condensate drain and Abandoned Uses

Air leakage and flow from the air consuming equipment in a facility is usually significant unless there is a regular system monitoring, leak detection and repair. Studies in the USA show that average leakage rated are 10 to 30 % of average compressor air consumption.

Air Dryer and Filter

The plant dew point was considered at the high side range from 42 - 45°C.  The inlet temperature to the dryer was detected at about 55°C during the assessment. Figures below shows thermographs of the compressor systems.

Thermograph of air pipe

Thermograph of compressor system

Efficiency

As seen in Figure, the power usage of the compressor system for a typical 1-hour period shows a baseline use of approximately 5kW and a peak usage of 21kW. The efficiency is relatively poor as the baseline is a significant portion of the power used.

Power usage for 1-hour time slot

The compressed air total installed capacity system of 20.0m3/min. The estimated average utility capacity flow demand capacities during the audit period was about 1.12 m3/min. The estimated highest and lowest flow demand capacities recorded were 1.67 m3/min and 0.91 m3/min respectively. The average discharge pressure recorded at the plant main header after the dryer during the assessment period was 9.5 barg (137.8 psig). The highest and lowest pressures were 10.0 barg (145 psig) and 9.0 barg (130.5 psig) respectively.

The following is a list of recommendation for the improvement:

- Replace the online filter elements which is one of the factors causing pressure drop.

- Investigate the high ambient temperature.

- Start a leakage detection and repair program.

BOILER/HOT WATER SYSTEM AND DISTRIBUTION

### SYSTEM DESCRIPTION

In order to provide a comprehensive analysis, we have analysed the quantity, quality, reliability and repeatability of the existing boiler and hot water system. The Heated Water System consists of 2 units of 1.8t fire-tube boilers and 2 units of Hot Water Heater units. Refer Figure below.

A brief site assessment of the existing boiler and hot water equipment was conducted and some preliminary data logging of the facility’s temperature. From these measurements and observations, an annual operating consumption estimate has been developed based on the observed operating profile and logged data on the assessment period.

These annual estimates will represent true annual costs only if conditions during the measurement period were typical of the entire annual period. Diesel fuel for the boiler and Hot Water Heater systems are delivered to the plant approximately every 6 weeks. The fuel is stored in a 5000ltr skid tank on site. The fuel is then pumped to the boiler and hot-water equipment. The readings and observations during the measurement period show the diesel-powered boiler and Hot Water Heater system used an average total of 2,100ltr between each fuel delivery.

### OBSERVATION AND FINDINGS

Boiler and Hot Water Heater site observation

Flue Gas loss

Boiler: The flue gas temperature was measured at a maximum 281.4°C. See Fig.

Hot Water Heater System: The flue gas temperature was measured at a maximum 84°C.

Both these systems release high temperature flue gas into the stack. Combined, the stack temperature would be in excess of 300°C. This makes the flue gas a recommended option for heat recovery. This economiser can then be used either for pre-heating the utility water input into the Hot Water Heater equipment or pre-heating the water supplied to the Hot Water Heater or warming the water in the hot water holding tanks.

An economiser pre-heating the utility water input into the Hot Water Heater can possibly perform the hot water heating task without requiring the Hot Water Heater operation. Further investigation is recommended.

Radiation and convection loss

The major energy losses in a boiler are from two sources. These are flue gas losses (which are covered above) and radiation and convection losses. Figures below shows the boiler main valve temperature.

Each boiler generates 1.8 t/hr steam. Referring to the ABMA chart, we can see that the loss of energy through radiation and convection is approximately 2.6% of the input fuel, in this case, the diesel fuel.

Leakage loss

With the age (over 15 years) of the Boiler system, leakages will be expected in the piping network and the steam traps.

Blow down loss

The blow-down water is not metered. The boiler blow-down water is drained to the drain via a 1.5-inch outlet pipe. This draining process is performed approximately 3 – 6 times per shift from 7am – 6pm. The blow down is released for approximately 30 seconds. Simple maths shows that about 18-20 litres blow-down water is released during each 30-sec draining.

Condensate loss

Condensate loss is the loss of the sensible heat in the liquid condensate returned to the boiler. Condensate can have as much as 16% of the total energy in the steam vapour. As such, condensate is an important energy conservation measure for boilers.

Un-insulated return pipes and valves lead to condensate loss. Visible cracks in the insulation were seen in the boiler and hot water piping network.

Following a list of recommendation for the improvement:

- Meter the amount of fuel fed to the Boiler and Hot Water Heater system

- Meter the amount of water fed to the Boiler and Hot Water Heater system

- Meter the amount of blow-down water from the Boiler

- Locate and repair steam and water leaks in the system

PROCESS EQUIPMENT

### SYSTEM DESCRIPTION

### OBSERVATION AND FINDINGS

AIR CONDITIONING AND MECHANICAL VENTILATION SYSTEM

### SYSTEM DESCRIPTION

Describe system

Example

The air conditioning system in the building is supplied by a number of air handling units in several plantrooms around the building, which serve manufacturing area, offices, canteen and certain parts of general area of the building.  The air conditioning system components include:

- Six (6) water-cooled chillers, cooling towers, chilled water pumps and condenser water pumps located at the air conditioning plant, outside the manufacturing block.

- Forty (40) air handling units (AHUs) located in the building AHU plant rooms on each floor

- Three Hundred and Eighty-Six (386) fan coil units (FCUs)

- Twelve (12) package air conditioners (PAUs).

The air conditioning for the plant is run for 24 hours a day.

sample

### BLOWER FAN SPECIFIC POWER

Describe findings

Example

The fan specific power is a measure of the air distribution system efficacy in W/m3.hr. It is the ratio of power consumed in Watt to the delivered air flow in cubic meter per hour. MS1525:2019 standard recommends that the power required by the entire fan system at design condition (for air flow >17,000 m3/hr) should not exceed 0.42 W/m3.h for AHU with operation time exceeding 750 hours a year.

The air flow data of twelve (12) AHUs have been obtained and compared with the MS 1525:2019. None of the AHUs with more than 17,000 m3/hr (10,000 cfm) air flowrate were found to be operating below the recommendation design value of 0.42 W/m3.hr. Table below shows the AHU air flow statistics data.

| No | AHU | sample Air Flow Rate, m3/hr |  | Fan Power, W | Fan Efficiency, W/m3hr |
| --- | --- | --- | --- | --- | --- |
|  |  | Design | Running |  |  |
| 1 | AHU-L1-MO1.4 | 28,237 | 17,193 | 8,668 | 0.50 |
| 2 | AHU-L1-MO1.8 | 34,503 | 33,361 | 9,833 | 0.29 |
| 3 | AHU-L1-MO1.9 | 24,451 | 9,539 | 7,439 | 0.78 |
| 4 | AHU-L2-MO1.1 | 37,392 | 25,554 | 9,768 | 0.38 |

sample

AIR CHANGE RATE AND AHU CAPACITY ANALYSIS

Describe findings

The air change analysis was carried out to determine the actual air change rate for all zones. The air change rate is based on how many times the air within a defined space is replaced in an hour.

Table below provides the calculated values of Air Change per Hour (ACR). Majority of the AHU has low ACH except for AHU PR 1/6 which serves OT room (designed minimum ACR of 20).  Minimum ACR is generally 6.0 ACH to prevent fungus growth. No major energy saving potential can be realized from ACR reduction.

| No | AHU | Capacity, Btu/hr | Air Flow Rate, m3/hr |  | Served Area, m2 | Air Change Per Hour (ACH) |  | Capacity Intensity, Btu/hr ft2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Design | Running |  | Design | Running |  |
| 1 | AHU-L1-M01.9 | 593,688 | 25,269 | 9,539 | 969.2 | 8.5 | 3.2 | 56.9 |
| 2 | AHU-L1-M01.8 | 812,056 | 34,503 | 33,361 | 1,600.9 | 7.0 | 6.8 | 47.1 |
| 3 | AHU-L1-M01.4 | 665,340 | 28,252 | 17,192 | 1,077.5 | 8.6 | 5.2 | 57.4 |
| 4 | AHU-ANX-L1A.3 | 535,684 | 22,824 | 5,853 | 925.2 | 8.1 | 2.1 | 53.8 |

### INDOOR AIR QUALITY

Describe findings

Example

The measurement for indoor air quality is done using a CO2 sensor. In most buildings CO2 sensors are installed in the return duct of the air conditioning system. The indoor air quality measured in the building is within the range of 158 and 381ppm. The maximum allowable reading in a room is 1000ppm after which the air in the room will become stale and will make the occupants feel sleepy due to lack of oxygen and fresh air.

sample

### TEMPERATURE AND RELATIVE HUMIDITY

Describe findings

Example

The temperature and relative humidity levels for each space were measured using temperature logger at selected area to represent the level of cooling and moisture content of the workspace. The minimum temperature is 19.3C and relative humidity levels are 50% and 85% respectively. Some areas are too cold and the temperature setting in these areas need to be increased. This could be due to failed control functionality of the VAV boxes or faulty temperature/RH sensors.

The measured RH of more than 70%, i.e. high moisture content in the air can lead to mould growth between cold and warm spaces such as door/window openings.

sample

sample

### OBSERVATION AND FINDINGS

From the air conditioning and ventilation energy audit works, it can be concluded as the following:

- The condition of the AHU plantroom needs to be improved as some plantroom 4 was found to be very dusty. This may cause the filters to get dirty very fast and load the AHU blower fan. Maintenance is done periodically.

- It was noted that condensation was seen in a few parts along the ducting. Source of the leakage or problem should be rectified immediately in order to reduce energy losses through loss of cooling.

- The need to compensate the centralized cooling with ACSU, shows that there is insufficient cooling provided by the centralized cooling system and the system needs to be reviewed.

- All air conditioning areas have automatic door closers and doors are always kept closed.

- The room temperatures are sufficient at time of audit but there have been complaints that it gets too warm when there are many people in the waiting area.

LIGHTING SYSTEM

### SYSTEM DESCRIPTION

The different types of lighting equipment and quantity is listed in the table below.

| Picture | Lamp Type | Lamp (W) | Ballast (W) | Qty | Area Used |
| --- | --- | --- | --- | --- | --- |
|  | 2 x 4 recessed with full reflectors | 36 | 8 | 350 | Office, Laboratory |
|  | 1 x 4 recessed with prismatic diffuser | 36 | 8 | 3350 | Staircase, Corridors |
|  | 1 x 4 bare channel | 36 | 8 | 300 | Car park |
|  | sample CFL | 18 | - | 60 | Lobby, Lifts |
|  | PAR | 60 | - | 15 | Rooftop |
|  | Incandescent | 100 |  | 80 | Decorative lighting for Foyer, Building Façade |
|  | PAR | 60 |  | 80 | Tasklight |

The lighting operating schedule of the building is listed below in the table.

| No | sample Description | Operation Hours |  |
| --- | --- | --- | --- |
|  |  | Start | Stop |
| Main Building |  |  |  |
| 1 | Office | 7:30am | 17:30pm |
| 2 | Lobby, Walkways | 7:00pm | 18:30pm |
| 3 | Car park | 7:00pm | 7:00am |

### LUX LEVEL

Describe findings

Example

The lux levels for each space was measured using a lux meter to indicate the level of lighting the occupants receive in the workspace. The average lighting levels in the office space is 240 lux. The maximum lighting level recorded is 1052 lux in one of the offices which is more than sufficient than the recommended values stipulated in the MS1525:2019, standard. The average lux levels in the common walkways and lobby is 175. See Appendix 5 for the room lux level readings.

The car park lighting was upgraded from 36W fluorescent tubes to 18W LED tubes. There is a separate report on the installation with the Facility Manager. The car park lighting is switched on 24 hours. There is sufficient lighting in the car park for some areas that are compensated with daylight due to openings within the car park area. See Figure 11.

sample

### OBSERVATION AND FINDINGS

From the lighting energy audit works, it can be concluded as the following:

- The number of lights can be reduced for the overlit areas.

- Car park lighting can be switched off during the day when there is sufficient daylight in the areas closest to the sides of the building openings.

PLANT MANAGEMENT SYSTEM

### SYSTEM DESCRIPTION

### OBSERVATION AND FINDINGS

CO-GENERATION BY BIOGAS/DIESEL/OTHERS AND DISTRIBUTION

# LOAD APPORTIONING AND ENERGY INDEX

Describe load apportioning

Example

sample

The load apportioning for the plant is listed in the table below and shown in the corresponding graph. The highest significant energy uses are the compressed air followed by the cooling tower, air conditioning for the plant and motors.

| Description | Energy kWh |
| --- | --- |
| Air compressor | 1847221.2 |
| Boiler | 591616.87 |
| Cooling tower | 890714.88 |
| Mill | 301754.97 |
| Motors | 664,240 |
| Air conditioning (plant) | 772960 |
| Air conditioning (office) | 56861 |
| Lighting (plant) | 335022 |
| Lighting (office) | 32941 |
| Office equipment | 19764 |

sample

# ENERGY SAVING MEASURES AND FINANCIAL EVALUATION

ESM No.1

It was found that…

Describe the problem

It is recommended that…

Describe the solution

Show the method of calculation and assumptions made:

Include:

- Energy consumption before

- Energy consumption after

- Cost savings in RM

- Investment costs in RM

- Simple Payback Period

- Percentage saving compared with system baseline and overall energy consumption baseline

Describe method statement/action plan to carry out implementation

Example

## ESM 1: Use Room/Return Air Humidity Input to Automatically Control the Glycol Chiller

As explained in the previous Energy Saving Measure, the glycol cooling coil in the MAHUs is used to control the humidity of the makeup outside air by further cooling the air after the chilled water coil.  The dehumidification process in the MAH’s is taken to an extreme, with the air being cooled by the glycol coil to about 5.5 oC.  The room humidity measured during the site inspection on 17 April 2018 was 44%, which is near the lower limit of humidity. Therefore, there is some leeway to allow a higher humidity in the building.

If the glycol cooling step in the MAH units is eliminated, the air is still cooled to around 11 oC by the remaining chilled water coils.  Because of the properties of saturated air at low temperatures, the difference in moisture content of air differs only marginally between these two temperatures, and will only result in an increase of approximately 5% in room RH, to about 49%, which is within allowed limits in the manufacturing areas. The effect of increased humidity within the conditioned space will be to reduce the likelihood of static electricity build-up, which may be considered an advantage in the manufacturing areas.

Under favorable conditions, the glycol chillers may be run at part load or not at all. To eliminate the possibility of the room Relative Humidity increasing above 50%, it is recommended that a humidity sensor in the room be used to control the glycol chillers.  The existing BMS measures humidity in occupied spaces, so a control signal from the BMS could be used to control the chillers.

The estimated annual energy saving achieved through this measure is 334,512 kWh with monetary value of RM69,579.  The budgeted investment required for implementing this measure is RM10,000 and the Payback period is 0.14 years (1.7 months).

ESM 2: Process Waste Recovery

The CO2 that is released into the atmosphere can be recovered and be converted to liquid.

Hydrogen is also released into the atmosphere in the tetrachloride process. This gas can be recovered and be used to burn in fuelcell technology for generation of electricity. There is approximately 160 ton/yr of hydrogen produced in the reduction process.

The potential savings in energy is RM1,315,000.00 with an estimated investment is RM2,500,000.00 and a payback period of 2 years.

Describe the step to implement ESM

### SUMMARY OF ENERGY SAVING MEASURES

Example

Seven (7) Energy Saving Measures (ESMs) have been identified in the Energy Audit conducted. By implementing all recommended Energy Saving Measures, the energy consumption for Building name can be reduced by about 23%, or 52,416kWh per year representing RM15,096 in monetary value. The estimated budget cost of implementing the Energy Saving Measures is RM27,042 with a payback period of about 1.79 years. The estimated savings, budget costs and Simple Payback Period of all recommended Energy Saving Measures, are listed in the table below.

sample

# ENERGY SAVING MEASURES IMPLEMENTATION PLAN (3 YEARS)

Describe method statement/action plan to carry out implementation

The table below lists the implementation measures to be carried out over the course of 3 years.

| Year | Measures | Percentage Reduced | Cost in RM | Time to Implement |
| --- | --- | --- | --- | --- |
| Base year |  |  |  |  |
| Year 1 | No Cost | 3% |  |  |
| ESM 1 |  |  |  | 3 months |
| ESM 2 |  |  |  | 3 months |
| Year 2 | Low/Medium Cost | 3% |  |  |
| ESM 3 |  |  |  | 7 months |
| Year 3 | High Cost | 4% |  |  |
| ESM 4 |  |  |  | 5 months |

Method statement

Example

ESM 1 – Replace existing lighting to LED

- Conduct an energy audit to measure current consumption

- Remove and replace existing lighting lamps/fixtures

- Install new lighting/fixtures

- Install energy meter for measurement and verification of new energy consumption

# CONCLUSION

Describe SEC Chart

Example

Using the estimated current annual energy consumption 232,050kWh and occupied areas, the current Specific Energy Consumtion (SEC) is xxx kWh/product and after implementing all recommended Energy Saving Measures to xxx kWh/product. The percentage reduction is 41%.

41% Reduction

sample

# VERIFICATION

|  |  | This Energy Audit Report is: |  |  |
| --- | --- | --- | --- | --- |
| prepared by: | checked by: |  | received by SEDA Malaysia | received by SEDA Malaysia |
|  | sample |  |  |  |
| Name: Position: Date: | Name: Position: Date: |  | Name: Position: Date: | Name: Position: Date: |